## Slide 1: Winterizing Cla-Val Valves (90 Series Focus)
TSID Work Session
10.21.2025

## Slide 2: Session Objectives
Why winterization is critical
Cla-Val 90 series overview
Instructions for flowing vs. no-flow conditions
Safety & inspection tips
Reactivation in spring
Q&A

## Slide 3: Why Winterize?
Freezing can block pilot system → valve failure
Cracking and damage to diaphragm or pilot tubing
Loss of flow control → irrigation disruption
Expensive repairs if valves freeze

## Slide 4
Common models: 90-01, 90-21, 90-99
Pilot-operated pressure reducing valves
Key components: valve body, diaphragm, pilot controls, strainer
Cla-Val 90 Series Overview

## Slide 5: Common Freeze Risks
Pilot tubing
Valve cover chamber
Strainer housings
Low-point water traps
Drain/test cocks

## Slide 6: Winterizing Under Flowing Condition
Add
Add insulation (commercial jackets, DIY wraps, straw, batts)
Add
Add heat (heat tape, small heaters in vault)
Best
Best: use both heat + insulation
Stop
Stop all leaks before insulating
Vent
Vent atmospheric drains outside insulation
Inspect
Inspect weekly during winter

## Slide 7: Winterizing Under No Flow Condition (Deactivation)
Shut off line pressure (close pilot cocks & downstream block valve)
Disconnect cover tubing, vent cover chamber → valve opens
Close upstream block valve → main valve closes
Remove plugs (cover + inlet/outlet bosses) to drain fully
Disconnect and drain all pilot tubing
Loosen pilot valve cover screws to drain cavities
Ensure all cavities are drained
Secure fittings for re-activation

## Slide 8: Reactivating in Spring
Replace all removed plugs
Reconnect drained pilot tubing
Tighten all fittings
Re-pressurize system (reverse shutoff sequence)
Bleed air from cover chamber & pilot high points
Follow standard startup procedure

## Slide 9: Safety Considerations
Depressurize
Always depressurize before disconnecting tubing
Handle
Handle insulation materials safely
Use
Use only UL-listed heaters/tape
Avoid
Avoid open flame near insulation or straw
Wear
Wear PPE when working in vaults

## Slide 10: Inspection Checklist
Weekly during winter (flowing condition)
Confirm insulation intact, no leaks or ice
Verify drains are vented correctly
Ensure heaters operating if installed

## Slide 11: Resources & Support
Cla-Val O&M Manuals (90-01, 90-21, 90-99)
contact for support
541-977-TSID
www.cla-val.com/